DIVISION 26 00 00				ELECTRICAL

SECTION 26 50 00 				LIGHTING

SECTION 26 56 00 				EXTERIOR LIGHTING

HELIO BOLLARD, SERIES 600 WITH SECURITY CORE

Part 1	General

- Summary

  - Section Includes:

    - Helio S10-P1 & SC30-P1 Security Bollard, Series 600, 6" diameter column, illuminated

    - Helio S10-P1 & SC30-P1 Security Bollard, Series 600, 6" diameter column, non-illuminated

- References

  - ASTMA 53 – Standard Specification for Pipe, Steel, Black, and Hot-Dipped, Zinc Coated, Welded and Seamless.

  - ASTMA 123 – Specification for Zinc (hot-dip galvanized) Coatings on Iron and Steel Products.

- Performance Requirements

  - Bollards must meet minimum level of S10- P1 or SC30-P1 as identified by the Standard Test Method for Vehicle Crash Testing of Perimeter Barriers. Manufacturer must provide documentation confirming that a finite element analysis has been completed for this product. A S10- P1 is equivalent to stopping a 5,000 lb. vehicle traveling at 10 mph in less than 1 meter and A SC30-P1 rating is equivalent to stopping a 2,430 lb. vehicle traveling at 30 mph in less than 1 meter.

- Submittals

  - Provide submittals in accordance with Section 01 33 00 – Submittal Procedures.

  - Product data: Manufacturer’s standard data sheets on each product to be used, including:

    - Manufacturer’s standard product literature.

    - Shop Drawings.

    - Installation instructions.

    - Maintenance instructions.

  - Submit finish samples for approval.

- Quality Assurance

  - Manufacturer Qualifications:

    - Minimum 15 years experience in the manufacture of outdoor lighting.

    - Provide reference list of at least ten major transportation authorities, municipalities, universities, or

other high-use public environments currently using site products fabricated by the manufacturer.

- Delivery, Storage and Handling

  - Handle products in accordance with manufacturer’s instructions.

  - Store products in manufacturer’s original packaging until ready for installation.

  - Protect products from impacts and abrasion during storage.

- Warranty

  - Provide manufacturer’s standard warranty:

    - Warranty terms: three years from date of invoice against defects in materials and workmanship.

Part 2   Products

- Manufacturer

  - Basis-of-design product: provide bollards based on the product named.

    - Helio Security Bollard, Series 600 by Forms+Surfaces

    - Manufacturer Contact:
Forms+Surfaces
30 Pine Street
Pittsburgh, PA 15223
phone: 800-451-0410

fax: 412-385-4715

email: sales@forms-surfaces.com

website: www.forms-surfaces.com

  - Security Bollards:

    - Materials:

      - Body: Stainless steel.

      - Base: Aluminum.

      - Head Cap (for illuminated bollards): Stainless steel casting.

      - Lens: .118” thick frosted acrylic.

      - LED Driver: Input voltage is 120-277 VAC nominal. Includes constant output current, with over-voltage, short circuit, overload protection, and has reverse phase, forward phase, and 0-10V dimming capabilities. Certifications include: IP66 (waterproof) enclosure, and Class 2 rated output (UL8750).

      - LED Light Engine (for illuminated bollards) (select color temperature below):

        - 360° Light Distribution:

            - 40W custom LED light engine.

            - Luminaire lumens: 424.

            - Color temperature (Select one color temperature below):

              - 3,000K.

              - 4,000K.

        - 180° Light Distribution:

            - 20W custom LED light engine.

            - Luminaire lumens: 158.

            - Color temperature (Select one color temperature below):

              - 3,000K.

              - 4,000K.

    - Finishes:

      - Body and Head Cap (Choose one finish below):

        - Satin with Ceramiloc treatment

        - Polyester powdercoat (Select one option below):

            - Standard Texture/Gloss from Forms+Surfaces Powdercoat Chart.

            - Custom RAL powdercoat color.

    - Dimensions: 40" high x 6" diameter.

    - Mounting (Choose one below):

      - S10-P1 Embedded Deep Set Security Core.

      - SC30-P1 Embedded Shallow Mount Security Core.

Part 3        Execution

  - Examination

- Verify that substrates are stable and capable of supporting the weight of items covered under this section.

- Verify that foundation, applied finishes, and adjacent construction are ready to receive bollards and are level, plumb, and square within tolerances acceptable to manufacturer.

- Verify that required utilities are in correct location and are of correct capacities for specified products.

  - Installation

- Install in accordance with manufacturer's installation instructions.

- Install in conformance to applicable ADA guidelines and End User’s established accessibility policies.

END OF SECTION